## Slide 1: Smart Cities – Group 12
Alex Blandón, Jonas Levi Doll, Max Concellon Marimon, Michelangelo Inzerilli
Notes: Hello, we‘re Group 12 and we were wondering:

## Slide 2
How can we be smarter,
at managing the energy of our buildings?
Notes: Homeowners traditionally relied on stable electricity prices with rigid contracts. Now, as gas boilers are replaced by heat pumps, EVs grow in popularity, and PV panels become mainstream, residential electricity bills are rising—but these changes also create opportunities to cut costs and increase self-sufficiency. The key question for households: How can we manage building energy more intelligently?

## Slide 3: Smart Buildings and Communities
Focus Stakeholders
Financial Impact
NPV Difference (20 y)
Energy Supply Costs per kWh
Environmental Impact
CO2 Emissions
Direct Embedded emissions Grid Vs PV (No credit)
Occupant Comfort
Energy Deficit
Building Min. Tº
DHW Top Layer Min. Tº
  House owners
  (Consumers)
DSO - Distribution System Operator
(Supplier)
Notes: To smartly manage energy in buildings and communities, we developed a controller using key KPIs: NPV over 20 years and energy supply costs for financial impact, a custom comfort indicator (energy deficit, minimum building temperature, and DHW top layer temperature), and embedded grid CO₂ emissions (excluding emissions avoided by exported PV power). These KPIs were selected based on stakeholder priorities—primarily homeowners and the DSO.

## Slide 4: E & C – Levels Analysis
Invidual strategies and combined controllers
for each Technology

## Slide 5: Optimising House 1012:
Price Arbitrage
Peak Shaving
Self Consumption
Combined Controller
0
1
Relative prices divided into bins depending on how expensive the price is
Heat Pump
1.
2.
3.
NPV:
+5.2 %
CO2:
- 4.8 %
Comfort:
+15.0 %

## Slide 6: Optimising House 1012:
Price Arbitrage
Peak Shaving
Self Consumption
Combined Controller
0
1
Relative prices divided into bins depending on how expensive the price is
Heat Pump
1.
2.
3.
Comfort:
+15 %
CO2:
- 4.8 %
NPV:
+5.2 %
Notes: In the case of the heat pump, peak shaving is most effective during periods of high electrical consumption, while self-consumption is activated when PV production peaks. Our price arbitrage strategy, based on detailed price analysis, only reduces the heating rate when the relative price is zero. While price arbitrage and peak shaving help lower energy supply costs and improve NPV, they also increase energy deficits and reduce occupant comfort. However, by integrating self-consumption into a combined controller, we add an energy buffer that significantly enhances comfort.
When implementing the final combined controller, we prioritize peak shaving first, followed by self-consumption, and finally price arbitrage—reflecting both their strategic importance and their placement within the heat pump system. As a result, this approach increases NPV by 5%, improves occupant comfort by 15%, and reduces environmental impact by 5%.

## Slide 7: Optimising House 1012:
Battery
Without subsidies economically not viable!
Chart: % Change Vs. Baseline
| NPV
Combined | -0.01031
Combined +50% Battery subsidies | 0.023032
NPV:
+2.3 %
CO2:
- 3.6 %
Energy supply cost:
-10.1 %
Chart: % Change Vs. Baseline
| SC | PA | PS
CO2 Emissions | -0.047033 | 0.0045827 | -0.031597
Energy supply cost | -0.046297 | -0.031308 | -0.096635
NPV | -0.052449 | -0.054363 | -0.012266
Price Arbitrage
Peak Shaving
Self Consumption

## Slide 8: Optimising House 1001:
EV
Price Arbitrage
Peak Shaving
Self Consumption
1.
2.
3.
Combined Controller EV + HP
+40%
-6%
-15%

## Slide 9: Smart Controller Deployment:
HP + EV
House 1001
House 1012
NPV:
+4.9 %
CO2:
- 12 %
Comfort:
+20.3 %
Costs per kWh
-20.5%
Full Charge Rate
X 2
PA
PA
PA
PA
PA
PA

## Slide 10: A – level analysis
Community energy system with smart control for every technology

## Slide 11: Energy Community
Energy supply costs:
-29.5 %
NPV:
+8.9 %
Individual Houses
Uncoordinated SC
Smaller DHW Tank (Less Thermal Inertia)
Baseline Community Vs Independent Homes
Higher SC
+35.6%
Lower Peak P Import
-23,34%
Before Smart Control
Shared Excess PV Generation
66% Larger Storage Tank
  More Thermal Inertia
12 Homes Vs. Community
Energy Community
CO2:
- 15.5%
Comfort:
-3,78 %
(Within limits)
Notes: A collection of independent households has several issues, such as uncoordinated self-consumption, and smaller DHW tanks distributed across all houses of the neighborhood. When implementing an energy community, even before smart controls we can have a better utilization of excess PV, and having a larger centralized storage tank provides more thermal inertia to the community. This means that even before applying smart controls, Energy communities have 35.6% higher SC than a collection of independent homes, and 23,3% lower Peak P imports. This ultimately leads to a reduction in costs of 30% and 9% higher NPV, a slight reduction in comfort of 3,7%, while still within hard limits of comfort, and CO2 emissions are reduced by 15.5%, meaning that Energy communities present a significant improvement over a collection of individual houses.

## Slide 12: Energy Community
Chart: % Change Vs. Baseline (12 Houses & Community)
| CO2 Emissions | Comfort Level | Peak Power | Average el. cost | NPV
Smart Homes | -0.12049 | 0.20302 | -0.049047 | -0.20498 | 0.05
Smart Community | -0.0012063 | -0.062524 | -0.16383 | -0.068778 | 0.018811
Smart Homes vs.
Smart Community
Smart Community
Building and DHW demand satisfied
+53% SC increase
Smart Control; Margin of Improvement
Larger Marginal Improvement From Making Independent Houses Smart
Better Absolute Values of KPIs in E Community
Notes: Whilst Energy communities present a massive improvement by themselves, we can still go a step farther and implement smart controls to improve their performance across several metrics. In our case, the final smart community focused on HP control, given that EV and Battery controls yielded less positive results, and combining technologies presented several challenges due to the interaction between the controls. With the best performing HP control, a smart energy community can satisfy the minimum building and DHW demands of residents, whilst we could increase SC by 53%.
When comparing the improvements of making an energy community smart against making a collection of homes smart, we can see that the marginal gains of making individual homes smart were higher than for making a community smart. As seen in this graph with the grey bar, smart homes have a largerg margin of improvement over the baseline than smart community for C=2 emissions, the comfort level, average electricity costs and the NPV, and only for the peak P reduction the energy community yields a larger margin of improvement. Ultimately, this whilst there is a larger marginal improvement from making independenr houses smart, you still have better absolute values of KPi's in an Energy community.

## Slide 13: Results and conclusion
Recommendations and future work on the smart city controllers

## Slide 14: Results and Conclusions
Technology Comparison
Heat Pump > EV Control > Battery
Difficult Cross-Technology Integration (Correlated effects)
Grid Purchases
Peak Import
and PV Export
Smart Households
Energy Community
DSO Perspective
Uncontrolled Energy Community > Smart Collection of Households
Smart Community Give Lower Margin of Improvement Than Smart Houses

## Slide 16: Thank you

## Slide 17: Backup Slides

## Slide 18: The Price Analysis – Price Arbitrage for the HP
Thresholds based on relative price distribution
Trade-off between energy consumption and load shifting
0
1
Chart: Building and Top Layer Temp
Chart: Building and SH Tank Temp

## Slide 19: Individual controllers
Tank size – 400 l.
Additional inertia for SC "dumping" and PS comfort
Little effect on PA
Heat Pump
Strategy | SC(DHW+SH)_400l | PA(DHW+SH)_200l | PS(APP_EV)_400l
Energy Deficit [kWh] | 45.9 | 61.1 | 57.8
CO2 Emissions [kg] | 4053 | 3874 | 4159
Building Min. T [Cº] | 20.5 | 20 | 20.5
DHW top layer Min. T [Cº] | 50.5 | 47.5 | 47.8
Peak Power [kW] | 6609 | 6425 | 5246
NPV difference [SEK] | +5 758 | +28 604 | +27 904
Self-Consumption
Price Arbitrage
Peak Shaving

## Slide 20: Combined Controller:
Tank size: 400 L (House 1012)
Additional inertia for SC "dumping" and PS comfort
Little effect on PA
Heat Pump
Self-Consumption
Price Arbitrage
Peak Shaving
Chart: % Change Vs. Baseline
| SC | PA | PS
CO2 Emissions | -0.022431 | -0.065605 | 0.0031356
Comfort Level (Deficit + Building T + DHW T) | 0.12264 | -0.13137 | -0.053317
NPV | 0.0078363 | 0.038929 | 0.037976

## Slide 21: Combined controller
Peak Shaving
Price Arbitrage
Self-Consumption
Chart: 
| Baseline | SC or PS or PA | Combined controller
CO2 Emissions | -0.15604 | 0.068767 | 0.61565
Comfort Level (Deficit + Building T + DHW T) | 0 | 0.010308 | 0
NPV | -0.078691 | 0.024224 | -0.12026
+39.1% SC
-14% Peak P
-10.6% SEK/kWh
EVs
NPV:
-20 %
CO2:
-10 %
Comfort:
+20 %

## Slide 22: Individual controllers
Battery
Strategy | SC | PA | PS
Energy Deficit [kWh] | 56.8 | 56.8 | 56.9
CO2 Emissions [kg] | 3951 | 4165 | 3997
Self consumption [%] | 47.7 | 40.2 | 38.4
Annual discharge [kWh] | 751 | 361 | 77.4
Peak Power [kW] | 6606 | 6606 | 4764
NPV difference [SEK] | -38539 | -39946 | -9013
Self-Consumption
Price Arbitrage
Peak Shaving

## Slide 23: Combined Controller
Peak Shaving
Price Arbitrage
Self-Consumption
Chart: % Change Vs. Baseline
| SC | PA | PS
CO2 Emissions | -0.047033 | 0.0045827 | -0.031597
Energy supply cost | -0.046297 | -0.031308 | -0.096635
NPV | -0.052449 | -0.054363 | -0.012266
Battery

## Slide 24: Combined Strategy
Heat Pump
Self Consumption
Net self production
Price Arbitrage
Peak Shaving
Relative el. price
Appliances and EV load
12 Building Average
+7.7% SC Increase
-2.2% Energy Consumption
-28.4% Peak P
Quantitative Results analysis (average price, energy supply costs, self consumption, energy deficit, HP switch on times, NPV value)
PA+PS PA+SC SC+PS PA+PS+SC
NPV Difference
386 798
Costs per kWh
-10.3%
CO2 emissions
-5.2 %
Energy deficit
-23.9%
Building Min. Tº
20.4 Cº (1.5% increase)
DHW Min. Tº
44.5 Cº (1% increase)
Comfort
Cost Savings

## Slide 25: Combined Strategy
Best Controller; EV + HP control
Bad Impact of BESS without subsidies
Combined Controllers
NPV Difference
410 276
Costs per kWh
-20.5%
CO2 emissions
-12 %
Energy deficit
-23.7%
Building Min. Tº
20 Cº (2% decrease)
DHW Min. Tº
47.7 Cº (1.4% decrease)
+3.8% SC Increase
-3.7% Energy Consumption
-4.9% Peak Power
Self Consumption
Price Arbitrage
Peak Shaving

## Slide 26: Energy Community
Heat Pump
Self-Consumption
1.78 SEK/kWh
Price Arbitrage
1.81 SEK/kWh
Peak Shaving
-22% Peak P
-1% E Consumption
20.5 / 57.3 Cº
+7% SC increase
1.71 SEK/kWh (-7%)
Combined Control
-16% Peak P
= E Consumption
20.5 / 57.4 Cº
+53% SC increase
1.71 SEK/kWh (-7%)
Comparison Vs. Baseline Energy Community
Moderate Improvements of SC and PA
Large Improvement of PS
Low Impact on Comfort

## Slide 27: Energy Community
Heat Pump
Strategy | SC(DHW+SH) | PA(DHW+SH) | PS(APP_EV) | SC+PA+PS
Energy Deficit [kWh] | 826 | 834 | 833 | 828
CO2 Emissions [ton] | 31.9 | 33 | 32.7 | 32.4
Building Min. T [Cº] | 20.6 | 20.5 | 20.5 | 20.5
DHW top layer Min. T [Cº] | 57.4 (52.4) | 59.5 (54.4) | 57.3 (52.3) | 57.4 (52.4)
Peak Power [MW] | 40 | 39.8 | 31.9 | 34.4
NPV difference [kSEK] | 62.8 | 40 | 172.6 | 142.8
Self-Consumption
Price Arbitrage
Peak Shaving
Combined Control

## Slide 28: Energy Community
Strategy (No control) | 12 Independent Households (Baseline) | Energy Community (Baseline)
Energy Deficit [kWh] | 637 | 829
CO2 Emissions [ton] | 39.4 | 33.3
Building Min. T [Cº] | 20.4 | 21.1
DHW top layer Min. T [Cº] | 48.4 | 59.5 (54.4)
Peak Power [MW] | 53.64 | 41.12
Average cost of electricity [SEK/kWh consumed] | 2.61 | 1.84
Individual Houses
Uncoordinated SC
Small Buildings/DHW Tanks (Less Thermal Inertia)
Higher Self-Consumption
+35.6% Increase
Before Smart Control
Shared PV Self-Consumption
More Thermal Inertia
  66% Larger Tank
  Larger Building (Unrealistic)
Baseline Vs. Community

## Slide 29: Energy Community
Strategy | 12 Independent Households (HP+EV) | Energy Community (HP)
Energy Deficit [%] | -23.7% | -0.1%
CO2 Emissions [%] | -12.0% | -2.5%
Building Min. T [Cº] | 20 | 20.5
DHW top layer Min. T [Cº] | 47.7 | 57.4
Peak Power [%] | -4.9% | -16.4%
Average cost of electricity in Y1 [SEK/kWh consumed] | 2.08 | 1.71
Individual Houses (Smart Control)
Uncoordinated SC
Small Buildings/DHW Tanks (Less Thermal Intertia)
NPV
+5%
XX
+X% Increase
Smart Energy Community
Shared PV Self-Consumption
More Thermal Inertia
  66% Larger Tank
  Larger Building (Unrealistic)
Smart Homes Vs. Smart Community